## Slide 1
Mechanical Stability of PV Modules
  —
    Jochen Markert, Frank Ensslen, Tobias Rist, Enzo Job, Ingrid Hädrich and Daniel Philipp
    SOPHIA-Workshop, Hasselt, 26.04.2024

## Slide 2: Motivation
Increased number of inquiries concerning glass breakages in PV power plants from all over the world
      Affected are:
        Framed/unframed modules in different mounting confidurations
        Module area > 2 m2
        Glass/glass designs with thicknesses ≤ 2.5 mm
      In contrast to mechanical failures in the past, problems occur after just a few months in the field
  Crack path (traced)

## Slide 3: Motivation
Glass Breakage
Cause of Glass Breakage
Assembly Error
Transport/ Handling
Environmental Impact

## Slide 4: Motivation
Glass Breakage
Cause of Glass Breakage
Assembly Error
Transport/ Handling
Environmental Impact

## Slide 5: Motivation
Glass Breakage
Cause of Glass Breakage
Assembly Error
Transport/ Handling
Environmental Impact
Contradictory development in PV industry
      Trend towards larger modules with ever thinner glass
Module Area
Glass Thickness
Trend to ≥ 3 m2
Trend to ≤ 2 mm

## Slide 6: Motivation
Glass Breakage
Cause of Glass Breakage
Assembly Error
Transport/ Handling
Environmental Impact
Glass as a brittle material seems to be a weak point in current module designs
Module Area
Glass Thickness
Trend to ≥ 3 m2
Trend to ≤ 2 mm
Glass Quality

## Slide 7: Motivation
Glass Breakage
Cause of Glass Breakage
Assembly Error
Transport/ Handling
Environmental Impact
Module Area
Glass Thickness
Trend to ≥ 3 m2
Trend to ≤ 2 mm
Glass Quality
Glass quality
      Edge quality
      Defect density
      Bending strength
      Prestressing of glass

## Slide 8: Motivation
Glass Breakage
Cause of Glass Breakage
Assembly Error
Transport/ Handling
Environmental Impact
Module Area
Glass Thickness
Trend to ≥ 3 m2
Trend to ≤ 2 mm
Glass Quality
Glass quality
      Edge quality
      Defect density
      Bending strength
      Prestressing of glass

## Slide 9: Qualification of Mechanical Stability
Glass-Industry
      Four-point- or double-ring-bending tests on a statistical relevant number of glass samples
Glass- vs. PV-Industry
PV-Industry
      Currently, a mechanical load test on a module in the certification process

## Slide 10: Glass Quality
Possible approaches:
      No direct determination (e.g. with 4-point-bending test) possible on laminate level
Determination in PV Modules

## Slide 11: Glass Quality
Possible approaches:
      No direct determination (e.g. with 4-point-bending test) possible on laminate level
      Fracture patterns: Qualitative classification of glass quality
Determination in PV Modules
Thermally Toughened Safety Glass (TTG) | Heat Strengthened Glass (HSG)
Homogeneous, fine-grained crack pattern | Inhomogeneous, coarse crack pattern with larger intact areas
[1]
[1]
[1] Wagner, E. Glasschäden: Oberflächenbeschädigungen, Glasbrüche in Theorie und Praxis, 2020.

## Slide 12: Glass Quality
Determination in PV Modules
Possible approaches:
      No direct determination (e.g. with 4-point-bending test) possible on laminate level
      Fracture patterns: Qualitative classification of glass quality
      Scattered light polariscope: Non-destructive measurement of the prestressing

## Slide 13: Glass Quality
Determination in PV Modules
Prestressed Glass
Compressive stress
Compressive stress
Tensile stress
Prism
Camera
Laser
Laser beam
Glass pane
Coupling fluid
Possible approaches:
      No direct determination (e.g. with 4-point-bending test) possible on laminate level
      Fracture patterns: Qualitative classification of glass quality
      Scattered light polariscope: Non-destructive measurement of the prestressing

## Slide 14: Results
Glass Samples – SCALP Measurements
30 glass samples for each type (360 x 360 mm2)
      Float Glass, 3 mm
      HSG, 4 mm
      HSG structured, 4 mm
      TTG, 3mm
SCALP Measurements

## Slide 15: Results
Glass Samples – SCALP Measurements + Double-Ring-Bending Test
Double-ring-bending test
SCALP measurements

## Slide 16: Results
PV Modules – SCALP Measurements
4 commercially available PV module types (~2 m2) were investigated:
Module Type | PV Module Design | Glass Thicknesses / mm
Type 1 | Glas/Glas | 2.0 / 2.0
Type 2 | Glas/Glas | 1.6 / 1.6
Type 3 | Glas/Glas | 1.6 / 1.6
Type 4 | Glas/Backsheet (Ref.) | 3.2 / -.-

## Slide 17: Results
PV Modules – SCALP Measurements
4 commercially available PV module types (~2 m2) were investigated:
Module Type | PV Module Design | Glass Thicknesses / mm
Type 1 | Glas/Glas | 2.0 / 2.0
Type 2 | Glas/Glas | 1.6 / 1.6
Type 3 | Glas/Glas | 1.6 / 1.6
Type 4 | Glas/Backsheet (Ref.) | 3.2 / -.-
Measurement of the glass surface stress:
      Measurable differences could be observed in the panes
      1.6 mm glass with higher prestress than 2 mm glass

## Slide 18: Results
PV Modules – Mechanical Load Tests Until Failure
ML Tests until failure in pressure direction
      4-point fixation at 20 % of the long module side without cross braces
        Free deflection allowed
      Homogeneous load distribution on the surface

## Slide 19: Results
PV Modules – Mechanical Load Tests Until Failure
Results:
      Module type with lowest surface stress showed significantly reduced failure loads
      Module with 1.6 mm panes showed comparable failure loads than the reference module with 3.2 mm TTG
Notes: Dünnes Glas kann Deformation besser aufnehmen als dickes, aber es scheint kritische Wert für die Glasvorspannung zu geben die bei homogener Belastung zum Tragen kommt

## Slide 20: Summary and Outlook
Preliminary Results
      SCALP can be used as an additional evaluation method for glass quality in PV modules
      Glass surface stress seems to show an influence on failure load of PV modules
      The basic expectation that 1.6 mm panes show generally lower surface stresses than thicker panes could not be verified
      With regard to homogeneous surface loads, no negative influence on the general module stability of thin glass modules could be observed in this series of tests
Notes: Übliche Qualitätsbestimmung mit Methoden aus Glasindustrie nicht möglich
Ausblick: Studie geplant mit großen Modulen gleiches Moduildesigns und konstanten Glasdicken. Annahme: Unterschiede in der Glasvorspannung (falls vorhanden) sollten besser aufflösbar sein
Inhomogene Lasten

## Slide 21
Thank you for your
Attention
  —

## Slide 22
Contact
  —
    Jochen Markert (M. Sc.)
    Department Module Characterization and Reliability
    Tel. +49 761 4588-5879
    jochen.markert@ise.fraunhofer.de
      Fraunhofer ISE
      Heidenhofstraße 2
      79110 Freiburg
      www.ise.fraunhofer.de

## Slide 23: References
    [1] Wagner, E. Glasschäden: Oberflächenbeschädigungen, Glasbrüche in Theorie und Praxis, 5., überarbeitete und erweiterte Auflage; Fraunhofer IRB Verlag: Stuttgart, 2020, ISBN 978-3-7388-0532-1.
    .

## Slide 24: Results
PV Glass – Influence of ARC
Pane with ARC on only one side
      15 measurement points on front and rear side

## Slide 25: Results
PV Glass – Influence of ARC
Pane with ARC on only one side
      15 measurement points on front and rear side
      Influence of ARC:
        Higher measurement inaccuracy
        Compressive stress slightly under-estimated with ARC coating  ≈ 10 MPa